## Process Calculation
Pump system hydraulic calculation — revision 2026-10-17
|  | Pipe leg | Suction | Discharge 1 | Discharge 2 | Discharge 3
Pump flow (m³/h) | 100 | Leg flow (m³/h) | 100 | 100 | 200 | 100
Density (kg/m³) | 1000 | Inner diameter (mm) | 150 | 150 | 200 | 200
Dynamic viscosity (mPa·s) | 1 | Straight length (m) | 6 | 128 | 256 | 0
Source vessel pressure (kPa absolute) | 100 | Roughness (mm) | 0.1 | 0.1 | 0.1 | 0.1
Vapor pressure (kPa absolute) | 30 | Sum of fitting K | 0 | 0 | 0 | 0
Source liquid level vs pump (m) | -4 | Active (1=yes, 0=no) | 1 | 1 | 1 | 0
Destination pressure (kPa absolute) | 100 | Flow / pump-flow ratio | 1 | 1 | 2 | 1
Destination level vs pump (m) | 5.5 | Velocity (m/s) | 1.5719 | 1.5719 | 1.7684 | 0
Pump efficiency (fraction) | 0.8 | Reynolds number | 235785.1009 | 235785.1009 | 353677.6513 | 0
Manufacturer NPSHr (m; example) | 2 | Darcy friction factor | 0.01939 | 0.01939 | 0.018009 | 0
Project NPSH margin (m; example) | 0.6 | Straight loss (kPa) | 0.95822 | 20.4419 | 36.0443 | 0
Gravity (m/s²) | 9.81 | Fitting loss (kPa) | 0 | 0 | 0 | 0
|  | Total loss (kPa) | 0.95822 | 20.4419 | 36.0443 | 0
Pump inlet static pressure (kPa abs) | 58.5663
Pump outlet static pressure (kPa abs) | 209.2057
Total differential head (m) | 15.3557
Hydraulic power (kW) | 4.1844
Pump shaft power (kW) | 5.2305
NPSH available (m) | 3.0379
NPSH available minus required (m) | 1.0379
NPSH assessment | Meets entered margin; verify curve
Boundary: large source/destination vessels, negligible surface velocities; signed levels relative to pump. Suction and first discharge leg must stay active. Enter parallel/header flow ratios explicitly.
Full circular pipe, incompressible Newtonian liquid. Darcy–Weisbach + ΣK. Colebrook for Re ≥ 4000; 64/Re below 2300; transition requires review. No update/copy button is required.
|  |  | Colebrook solver | Colebrook solver | Colebrook solver | Colebrook solver
|  |  | 7 | 7 | 7 | 7
|  |  | 7.188 | 7.188 | 7.4665 | 0
|  |  | 7.1812 | 7.1812 | 7.4511 | 0
|  |  | 7.1814 | 7.1814 | 7.4516 | 0
|  |  | 7.1814 | 7.1814 | 7.4516 | 0
|  |  | 7.1814 | 7.1814 | 7.4516 | 0
|  |  | 7.1814 | 7.1814 | 7.4516 | 0
|  |  | 7.1814 | 7.1814 | 7.4516 | 0
|  |  | 7.1814 | 7.1814 | 7.4516 | 0
|  |  | 7.1814 | 7.1814 | 7.4516 | 0
|  |  | 7.1814 | 7.1814 | 7.4516 | 0

## Results Summary
Current hydraulic results
Pump flow (m³/h) | 100
Density (kg/m³) | 1000
Dynamic viscosity (mPa·s) | 1
Source vessel pressure (kPa absolute) | 100
Vapor pressure (kPa absolute) | 30
Source liquid level vs pump (m) | -4
Destination pressure (kPa absolute) | 100
Destination level vs pump (m) | 5.5
Pump efficiency (fraction) | 0.8
Manufacturer NPSHr (m; example) | 2
Project NPSH margin (m; example) | 0.6
Pump inlet static pressure (kPa abs) | 58.5663
Pump outlet static pressure (kPa abs) | 209.2057
Total differential head (m) | 15.3557
Hydraulic power (kW) | 4.1844
Pump shaft power (kW) | 5.2305
NPSH available (m) | 3.0379
NPSH available minus required (m) | 1.0379
NPSH assessment | Meets entered margin; verify curve
These are linked results, not a frozen certified selection. Confirm inputs, manufacturer curve and NPSH margin before specifying a pump.

## Results Output
Pump duty review — printable results
Pump flow (m³/h) | 100
Density (kg/m³) | 1000
Dynamic viscosity (mPa·s) | 1
Source vessel pressure (kPa absolute) | 100
Vapor pressure (kPa absolute) | 30
Source liquid level vs pump (m) | -4
Destination pressure (kPa absolute) | 100
Destination level vs pump (m) | 5.5
Pump efficiency (fraction) | 0.8
Manufacturer NPSHr (m; example) | 2
Project NPSH margin (m; example) | 0.6
Pump inlet static pressure (kPa abs) | 58.5663
Pump outlet static pressure (kPa abs) | 209.2057
Total differential head (m) | 15.3557
Hydraulic power (kW) | 4.1844
Pump shaft power (kW) | 5.2305
NPSH available (m) | 3.0379
NPSH available minus required (m) | 1.0379
NPSH assessment | Meets entered margin; verify curve
These are linked results, not a frozen certified selection. Confirm inputs, manufacturer curve and NPSH margin before specifying a pump.

## Home
Pump system hydraulic workbook
1. Enter fluid, vessel conditions and pipe legs in Process Calculation.
2. Yellow cells are inputs; blue result cells recalculate automatically in Excel.
3. Review the live Results Summary or print Results Output. No macros or missing update button.
Pressures are absolute in kPa. Levels are signed metres relative to pump center.
Zero roughness, zero static difference and zero fitting losses are valid. Negative NPSH margin stays negative.
NPSHr and the required margin are duty-specific manufacturer/project inputs; supplied values are examples.
Revised 2026-10-17. Tested in Microsoft Excel 16. WPS and LibreOffice have not been tested.
Method: Darcy–Weisbach, Colebrook–White, Bernoulli pressure balance; single-phase Newtonian liquid.