## Main Calculator
AutomaticPump Head Calculator
BasicParameters:
Colebrook solver
| Pump Flow Rate: | 0.01 | m³/s | [6 empty] | 7
| Pump Medium / Fluid: |  |  | Fluid Density ρ, | 1000 | ,kg/m³ |  |  |  | 6.7781
|  |  |  | Fluid Viscosity μ, | 0.001 | Pa·s |  |  |  | 6.7875
| Discharge Height, Hd |  | 10 | (Unit: m) | [5 empty] | 6.7871
| Suction Height, Hs |  | 5 | (Unit: m) | Reynolds Number, Re = | 127323.9545 |  |  |  | 6.7871
| Pump Discharge Pressure Pd |  | 1 | Unit: MPa | Pipe Resistance | 18.1231 |  |  |  | 6.7871
| Pump Suction Pressure Ps |  | 0.2 | Unit: MPa | [5 empty] | 6.7871
6.7871
| Pipe Inner Diameter d |  | 0.1 | (Unit: m) | [5 empty] | 6.7871
| Straight Pipe Length l |  | 1000 | (Unit: m) | [5 empty] | 6.7871
| Pipe Roughnessε |  | 0.0001 | (Unit: m | [5 empty] | 6.7871
| Local Resistance Coeff., ζ |  | 0.75
| Flow Velocityv |  | 1.2732 | Unit: m/s) |  |  |  |  | Darcy factor | 0.021709
Additional end-loss K |  |  | 1.5
[6 empty] | Calculation Result | 104.6725 | Unit: m
Tip:
Hd and Hs are signed vessel liquid levels relative to pump center: positive above. Static elevation difference = Hd − Hs.
Pd and Ps are vessel gauge pressures in MPa. Density kg/m³; viscosity Pa·s; diameter and roughness m.
Colebrook–White for Re ≥ 4000; 64/Re for Re < 2300. Transition results require review. The separate end-loss K=1.5 is an editable example assumption, not a hidden addition.

## Pipe Roughness Ref
Pipe Roughness
| Pipe Category |  | Absolute Roughness ε/mm | Pipe Category |  | Absolute Roughness ε/mm
|  | Seamless brass/steel/lead pipe | 0.01–0.05 |  | Clean glass tube | 0.0015–0.01
|  | New seamless steel, galvanized iron pipe | 0.1–0.2 | Non- | Rubber hose | 0.01–0.03
| Metal | New cast iron pipe | 0.3 | Metal | Wood stave pipe | 0.25–1.25
|  | Slightly corroded seamless steel pipe | 0.2–0.3 |  | Vitrified clay drainage pipe | 0.45–6.0
| Pipe | Significantly corroded seamless steel pipe | ≥ 0.5 | Pipe | Smooth-Finished Cement Pipe | 0.33
|  | Old cast iron pipe | ≥ 0.85 |  | Asbestos cement pipe | 0.03–0.8
Ranges restored as reference intervals; confirm actual pipe condition. Values here are in mm; divide by 1000 for the main calculator roughness input.

## Local Resistance Ref
Local Resistance Coefficient ζ Values for Common Fittings & Valves
Fitting / Valve Name | ζ Value
Standard Elbow | 45°ζ0.35 | [12 empty] | 90°ζ0.75
90° Square Elbow | 1.3
180° Return Bend | 1.5
Union | 0.4
Bend | φ | 30° |  |  |  |  | 45° |  |  |  | 60° |  |  |  | 75° |  | 90° |  |  |  |  | 105° |  |  |  |  | 120°
R/d
| 1.5 | 0.08 |  |  |  |  | 0.11 |  |  |  | 0.14 |  |  |  | 0.16 |  | 0.175 |  |  |  |  | 0.19 |  |  |  |  | 0.2
| 2 | 0.07 |  |  |  |  | 0.1 |  |  |  | 0.12 |  |  |  | 0.14 |  | 0.15 |  |  |  |  | 0.16 |  |  |  |  | 0.17
Sudden Expansion | A 1/A 2 | 0 |  |  | 0.1 |  | 0.2 |  |  |  | 0.3 |  | 0.4 |  | 0.5 |  | 0.6 |  | 0.7 |  |  | 0.8 |  |  | 0.9 |  | 1
| ζ | 1 |  |  | 0.81 |  | 0.64 |  |  |  | 0.49 |  | 0.36 |  | 0.25 |  | 0.16 |  | 0.09 |  |  | 0.04 |  |  | 0.01 |  | 0
Sudden Contraction | A 1/A 2 | 0 |  |  | 0.1 |  | 0.2 |  |  |  | 0.3 |  | 0.4 |  | 0.5 |  | 0.6 |  | 0.7 |  |  | 0.8 |  |  | 0.9 |  | 1
| ζ | 0.5 |  |  | 0.47 |  | 0.45 |  |  |  | 0.38 |  | 0.34 |  | 0.3 |  | 0.25 |  | 0.2 |  |  | 0.15 |  |  | 0.09 |  | 0
Standard Tee Pipe
| ζ=0.4 | [6 empty] | ζ=1.5 | [6 empty] | ζ=1.3 | [6 empty] | ζ=1
Gate Valve | Full Open | [6 empty] | 3/4 Open | [7 empty] | 1/2 Open | [6 empty] | 1/4 Open
| 0.17 | [6 empty] | 0.9 | [7 empty] | 4.5 | [6 empty] | 24
Globe Valve | Full Openζ=6.4 | [14 empty] | 1/2 Openζ=9.5
(Globe Valve)
Butterfly Valve | a |  | 5° |  |  | 10° |  |  | 20° |  |  | 30° |  |  |  | 40° |  | 45° |  |  | 50° |  |  | 60° |  |  | 70°
| ζ |  | 0.24 |  |  | 0.52 |  |  | 1.54 |  |  | 3.91 |  |  |  | 10.8 |  | 18.7 |  |  | 30.6 |  |  | 118 |  |  | 751
Plug Cock | θ |  |  | 5° | [5 empty] | 10° | [5 empty] | 20° |  |  |  | 40° | [5 empty] | 60°
| ζ |  |  | 0.24 | [5 empty] | 0.52 | [5 empty] | 1.56 |  |  |  | 17.3 | [5 empty] | 206
Check Valve | Swing Check ζ = 2 | [14 empty] | Ball Check ζ = 70
Angle Valve (90°) | 5
Foot Valve | 1.5
Strainer | 2
(or Strainer)
Water Meter (disc type) | 7
Pipe Valve Spec Typevaries widely Water machining precisionis large Therefore Coefficientζ's variation rangeis large Value Value For Other Pipe Valveζ Value Referencerelevant references